## INFO-INSTRUCTIONS
GENERAL INFORMATION
1. The spreadsheet is a tool for LMVx curve commissioning on gaseous fuels. It provides an orderly way to record and visualize data while using the AZL for commissioning. The different tabs are tailored for different applications.
2. For LMV5 applications, 10 points are used. This is not adjustable in the spreadsheet. For LMV3 applications, 9 points are used, which is also not adjustable in the spreadsheet.
3. This spreadsheet is designed to be used with an accurate fuel flow meter. Approximate burner head pressure for each point is also provided based on high fire head pressure using the square root law for the relationship between flow and pressure differential. Burner head pressure should only be used as a "better than nothing" way to estimate fuel flow, and is typically not adequate for setting up burners that use O2 trim.
4. Green shaded cells are to be filled out before commissioning, ideally based on "known" information. However, many burners do not perform to published high fire output and turndown specifications. Most burners must be run up to high fire and down to low fire to get the actual high fire and the actual turndown performance. It is recommended to find the actual high fire and the actual low fire (Section 4 of LMV5 Technical Instructions) before filling out the green shaded cells.
5. If the spreadsheet is in "Auto Calc" mode, gas flow and load will be linearly increased and equally spaced from low fire to high fire. The actual values will be based off of the numbers entered for high fire burner output and turndown.
6. If the spreadsheet is in "Manual Entry" mode, load will be calculated based on the fuel flow that is manually entered and the high fire burner output. The turndown number has no effect in this mode.
7. For O2 Trim on Mesh Burners where the LMV5 is set up to have Point 2 as low fire, Point 1 still must exist even if the gap between Point 1 and Point 2 is smaller. This is why the tab for O2 Trim on Mesh Burners has the "Load Reduction for Point 1" option. The gap between Point 1 and Point 2 can be reduced so that the overall turndown of the burner is only slightly limited. For the O2 Trim on Mesh Burners tab, the "Burner Turndown" is calculated between Point 2 and Point 10. On all other LMV5 tabs, "Burner Turndown" is calculated between Point 1 and Point 10.
GENERAL INSTRUCTIONS
1. Select the appropriate spreadsheet tab. The LMV52 O2 trim tab can be used for an LMV52 that has VSD but no O2 trim. The LMV52 O2 Trim Mesh Burner tab can also be used for high percentage FGR burners that are not a mesh type of burner.
2. Unless the true burner high fire output and turndown are definitely known, find these values by running the burner at these points before the ratio curve commissioning begins. Once the values are known, input these into the appropriate green cells. For convenience, an optional input cell is included that will calculate the turndown number based off of the high fire output and the entered low fire fuel flow. Entering the information in the green cells will set the fuel flow targets for the burner at each point.
3. Commission the ratio control curve for safe, efficient combustion for Point 1 thru Point 10. Record data for each point in the yellow shaded cells. If the burner in question will have O2 trim, the ratio control curve can be used to "probe" the rich and lean limits of the burner and these values should be recorded in the spreadsheet for later use. If the burner in question is also a low (NOx) emissions burner, the Target O2 corresponding to emissions compliance will also need to be probed and the values recorded in the spreadsheet for later use. See Section 4 (Commissioning) and Section 6 (O2 Trim) for more information on O2 trim burners.
4. If the O2 trim is being commissioned, record the data in the blue shaded cells. Recording the O2 ratio control, O2 control and Standard Val should result in the lambda factor being calculated. The lambda factor should be reasonably linear. More variance in the lambda factor from point to point can be expected if using FGR and if the gap between the O2 ratio control and the O2 control curves is less than 0.5%. As a guideline, adjacent points having a difference of 0.20 or less would be considered good. A difference of 0.50 for adjacent points would be unacceptable for most burners. The standard deviation for the lambda factor curve (all the points) should be in the range of 0.1 (good) to 0.35 (borderline acceptable).
5. For dual fuel burners where the second fuel is oil, airflow matching can be used to approximate the oil flow. This is done by using a flow meter for the gas and commissioning the gas first. The same air damper / VSD positions and the same load numbers from the commissioned gas curve can then be used for the oil curve, which should yield a linear increase in the oil flow as firing rate increases.
6. O2 trim is rarely done when firing #2 oil, since this is typically a back-up fuel. As such, this spreadsheet does not cover setting up O2 trim on #2 oil. If O2 trim is being done on oil, an oil flow meter should also be utilized.

## LMV3 Basic
Indicates information to be filled out before commissioning ratio control curves
Indicates information to be filled out during commissioning of ratio control curves
| LMV3 Basic Burner-Gas | [8 empty] | Units | Input Data |  | Units | Input Data
Application Info | Burner Output at High Fire | [8 empty] | MM BTU / HR | 10 | Gas Pressure upstream of Regulator | PSIG
| Burner Head (manifold) Pressure at High Fire | [8 empty] | IN WC | 10 | Gas pressure upstream of Firing Rate Valve at Low fire | IN WC
| Burner Turndown | [8 empty] | xx to 1 | 10 | Gas pressure upstream of Firing Rate Valve at High fire | IN WC
| Heating Value of Gas | [8 empty] | BTU / SCFH | 1000 | Furnace pressure at Low fire | IN WC
| Boiler Efficiency | [8 empty] | % | 85 | Furnace pressure at High Fire | IN WC
Actuator / VSD Ratio Control Curves
|  | These cells are calculated from the "Application Info" cells above | [5 empty] | Manually Input during Ratio Control Curve Commissioning
CURVE POINTS | LMV Curve Point | Gas flow to Burner (Auto Calc) | Burner Output |  | Burner Head Pressure (Approx) | Boiler Output @ Efficiency | Steam Flow 230o F feed 100 PSIG Steam (Approx) | Air Act Pos | Fuel Act. Pos | VSD Speed
| # | SCFH | MM BTU /HR | MW | IN WC | BHP | lb/hr | Deg | Deg | %
| 1 | 1000 | 1 | 0.2928 | 0.1 | 25.3921 | 857.9792
| 2 | 2125 | 2.125 | 0.6222 | 0.45156 | 53.9582 | 1823.2058
| 3 | 3250 | 3.25 | 0.9516 | 1.0563 | 82.5243 | 2788.4324
| 4 | 4375 | 4.375 | 1.281 | 1.9141 | 111.0904 | 3753.659
| 5 | 5500 | 5.5 | 1.6104 | 3.025 | 139.6565 | 4718.8856
| 6 | 6625 | 6.625 | 1.9398 | 4.3891 | 168.2226 | 5684.1122
| 7 | 7750 | 7.75 | 2.2692 | 6.0063 | 196.7886 | 6649.3389
| 8 | 8875 | 8.875 | 2.5986 | 7.8766 | 225.3547 | 7614.5655
| 9 | 10000 | 10 | 2.928 | 10 | 253.9208 | 8579.7921

## LMV51 Basic
Indicates information to be filled out before commissioning ratio control curves
Indicates information to be filled out during commissioning of ratio control curves.
[15 empty] | Units | Input Data
| LMV51 Basic burner - Gas | [9 empty] | Units |  | Input Data | If needed : Gas flow at Low Fire (to calc turndown number) | SCFH | 2000 | 5 | to 1
Application Info | Burner Output at High Fire | [9 empty] | MM BTU / HR |  | 10 | Gas pressure upstream of Regulator | PSIG
| Burner Head (manifold) pressure at High Fire | [9 empty] | IN WC |  | 10 | Gas pressure upstream of Firing Rate Valve at Low fire | IN WC
| Burner Turndown | [9 empty] | xx to 1 |  | 10 | Gas pressure upstream of Firing Rate Valve at High fire | IN WC
| Heating Value of Gas | [9 empty] | BTU / SCFH |  | 1000 | Furnace pressure at Low fire | IN WC
| Boiler Efficiency | [9 empty] | % |  | 82 | Furnace pressure at High Fire | IN WC
| LMV Load Numbers : Base on Manual Entry or Auto Calc Gas flow? (M = Manual Entry, A = Automatic Calc) | [9 empty] | A or M |  | A
Actuator / VSD Ratio Control Curves
|  | Manual Input | These cells are calculated from the "Application Info" cells above | [6 empty] | Manually Input during Ratio Control Curve Commissioning
CURVE POINTS (Ratio Control) | LMV Curve Point | Gas flow to Burner (Manual Entry / Paste) | Gas flow to Burner (Auto Calc) | LMV Load at Curve Point | Burner Output |  | Burner Head Pressure (Approx) | Boiler Output @ Efficiency | Steam Flow 230o F feed 100 PSIG Steam (Approx) | Air Act Pos | Fuel Act. Pos | Aux Act Pos
| # | SCFH | SCFH | % | MM BTU /HR | MW | IN WC | BHP | lb/hr | Deg | Deg | Deg
| 1 | 1111 | 1000 | 10 | 1 | 0.2928 | 0.1 | 24.4959 | 827.6976
| 2 | 2000 | 2000 | 20 | 2 | 0.5856 | 0.4 | 48.9918 | 1655.3952
| 3 | 2500 | 3000 | 30 | 3 | 0.8784 | 0.9 | 73.4877 | 2483.0928
| 4 | 22 | 4000 | 40 | 4 | 1.1712 | 1.6 | 97.9836 | 3310.7904
| 5 | 2345 | 5000 | 50 | 5 | 1.464 | 2.5 | 122.4795 | 4138.4879
| 6 | 4000 | 6000 | 60 | 6 | 1.7568 | 3.6 | 146.9754 | 4966.1855
| 7 | 4500 | 7000 | 70 | 7 | 2.0496 | 4.9 | 171.4712 | 5793.8831
| 8 | 5000 | 8000 | 80 | 8 | 2.3424 | 6.4 | 195.9671 | 6621.5807
| 9 | 9000 | 9000 | 90 | 9 | 2.6352 | 8.1 | 220.463 | 7449.2783
| 10 | 8000 | 10000 | 100 | 10 | 2.928 | 10 | 244.9589 | 8276.9759

## LMV52 O2 Trim
Indicates information to be filled out before commissioning ratio control curves
Indicates information to be filled out during commissioning of ratio control curves.
Indicates information to be filled out during commissioning of O2 trim.
[18 empty] | Units | Input Data
| LMV52 with O2 Trim - Gas | [9 empty] | Units |  | Input Data |  |  |  | If needed : Gas flow at Low Fire (to calc turndown number) | SCFH | 2000 | 30.1015 | to 1
Application Info | Burner Output at High Fire | [9 empty] | MM BTU / HR |  | 60.203 |  |  |  | Gas pressure upstream of Regulator | PSIG
| Burner Head (manifold) pressure at High Fire | [9 empty] | IN WC |  | 10 |  |  |  | Gas pressure upstream of Firing Rate Valve at Low fire | IN WC
| Burner Turndown | [9 empty] | xx to 1 |  | 6 |  |  |  | Gas pressure upstream of Firing Rate Valve at High fire | IN WC
| Heating Value of Gas | [9 empty] | BTU / SCFH |  | 1000 |  |  |  | Furnace pressure at Low fire | IN WC
| Boiler Efficiency | [9 empty] | % |  | 82 |  |  |  | Furnace pressure at High Fire | IN WC
| LMV Load Numbers : Base on Manual Entry or Auto Calc Gas flow? (M = Manual Entry, A = Automatic Calc) | [9 empty] | A or M |  | a
Actuator / VSD Ratio Control Curves
|  | Manual Input | These cells are calculated from the "Application Info" cells above | [6 empty] | Manually Input during Ratio Control Curve Commissioning
CURVE POINTS (Ratio Control) | LMV Curve Point | Gas flow to Burner (Manual Entry / Paste) | Gas flow to Burner (Auto Calc) | LMV Load at Curve Point | Burner Output |  | Burner Head Pressure (Approx) | Boiler Output @ Efficiency | Steam Flow 230o F feed 100 PSIG Steam (Approx) | Air Act Pos | Fuel Act. Pos | VSD Speed | Aux 1 Act Pos | Aux 2 Act Pos | Aux 3 Act Pos | Set Ratio control @ this O2 value (-0, +0.2%)
| # | SCFH | SCFH | % | MM BTU /HR | MW | IN WC | BHP | lb/hr | Deg | Deg | % | Deg | Deg | Deg | % O2 Wet
| 1 | 6250 | 10033.8333 | 16.6667 | 10.0338 | 2.9379 | 0.27778 | 245.7877 | 8304.9796 | [6 empty] | 2
| 2 | 8333.3333 | 15608.1852 | 25.9259 | 15.6082 | 4.5701 | 0.67215 | 382.3364 | 12918.8572 | [6 empty] | 2
| 3 | 10416.6667 | 21182.537 | 35.1852 | 21.1825 | 6.2022 | 1.238 | 518.8851 | 17532.7348 | [6 empty] | 2
| 4 | 12000 | 26756.8889 | 44.4444 | 26.7569 | 7.8344 | 1.9753 | 655.4339 | 22146.6124 | [6 empty] | 2
| 5 | 15645 | 32331.2407 | 53.7037 | 32.3312 | 9.4666 | 2.8841 | 791.9826 | 26760.49 | [6 empty] | 2
| 6 | 16666.6667 | 37905.5926 | 62.963 | 37.9056 | 11.0988 | 3.9643 | 928.5313 | 31374.3675 | [6 empty] | 2
| 7 | 17340 | 43479.9444 | 72.2222 | 43.4799 | 12.7309 | 5.216 | 1065.08 | 35988.2451 | [6 empty] | 2
| 8 | 20833.3333 | 49054.2963 | 81.4815 | 49.0543 | 14.3631 | 6.6392 | 1201.6288 | 40602.1227 | [6 empty] | 2
| 9 | 22916.6667 | 54628.6481 | 90.7407 | 54.6286 | 15.9953 | 8.2339 | 1338.1775 | 45216.0003 | [6 empty] | 2
| 10 | 23000 | 60203 | 100 | 60.203 | 17.6274 | 10 | 1474.7262 | 49829.8779 | [6 empty] | 2
%O2 Control - Alarm Curves
From Above |  |  | Based on O2 Alarm Rich and O2 Ratio |  | Based on burner capabilities |  | As saved in the LMV52 |  |  | Emissions Data from Exhaust Gas Analyzer @ O2 Ratio Control |  |  | Emissions Data from Exhaust Gas Analyzer @ O2 Control
CURVE POINTS (O2 Control-Alarm) | LMV Curve Point | LMV Load at Curve Point | Target for O2 Control |  | O2 Alarm (Rich Limit)* | O2 MaxValue (Lean Limit) | O2 Ratio Control | O2 Control | Standard Val | O2 (Dry) | CO | Nox | O2 (Dry) | CO | Nox
| # | % | % O2 Wet |  | % O2 Wet |  | % O2 Wet |  | % | % | PPM | PPM | % | PPM | PPM
| 1 | 16.6667 | MAX | MIN |  |  | Cannot trim on Point 1 |  |  | Cannot trim on Point 1 |  |  | Cannot trim on Point 1
| 2 | 25.9259 | 1 | 0.5
| 3 | 35.1852 | 1 | 0.5
| 4 | 44.4444 | 1 | 0.5
| 5 | 53.7037 | 1 | 0.5
| 6 | 62.963 | 1 | 0.5
| 7 | 72.2222 | 1 | 0.5
| 8 | 81.4815 | 1 | 0.5
| 9 | 90.7407 | 1 | 0.5
| 10 | 100 | 1 | 0.5
* Determined during commissioning of Ratio Control Curves. Not recommended to exceed 200 PPM CO or run less than 1.0% O2 (as measured by a calibrated, external exhaust gas analyzer).
LMV52 Load | Lambda Ratio control Curve | Lambda O2 control curve | Lambda factor | Average Lambdafactor | Standard Dev
| Ratio | Setpoint
25.9259 | 1.0528 | 1.0528 | 0 | 0 | 0
35.1852 | 1.0528 | 1.0528 | 0 | 0
44.4444 | 1.0528 | 1.0528 | 0 | 0
53.7037 | 1.0528 | 1.0528 | 0 | 0
62.963 | 1.0528 | 1.0528 | 0 | 0
72.2222 | 1.0528 | 1.0528 | 0 | 0
81.4815 | 1.0528 | 1.0528 | 0 | 0
90.7407 | 1.0528 | 1.0528 | 0 | 0
100 | 1.0528 | 1.0528 | 0 | 0

## LMV52 O2 Trim Mesh Burner
Indicates information to be filled out before commissioning ratio control curves
Indicates information to be filled out during commissioning of ratio control curves.
Indicates information to be filled out during commissioning of O2 trim.
[18 empty] | Units | Input Data
| LMV52 with O2 Trim on Ultra Low Nox and Mesh Burners - Gas | [9 empty] | Units |  | Input Data |  |  |  | If needed : Gas flow at Low Fire (to calc turndown number) | SCFH | 2000 | 5 | to 1
Application Info | Burner Output at High Fire | [9 empty] | MM BTU / HR |  | 10 |  |  |  | Gas pressure upstream of Regulator | PSIG
| Burner Head (manifold) pressure at High Fire | [9 empty] | IN WC |  | 10 |  |  |  | Gas pressure upstream of Firing Rate Valve at Low fire | IN WC
| Burner Turndown | [9 empty] | xx to 1 |  | 10 |  |  |  | Gas pressure upstream of Firing Rate Valve at High fire | IN WC
| Heating Value of Gas | [9 empty] | BTU / SCFH |  | 1000 |  |  |  | Furnace pressure at Low fire | IN WC
| Boiler Efficiency | [9 empty] | % |  | 85 |  |  |  | Furnace pressure at High Fire | IN WC
| Load Reduction for Point 1 (subtracted from point 2) | [9 empty] | SCFH |  | 500
| LMV Load Numbers : Base on Manual Entry or Auto Calc Gas flow? (M = Manual Entry, A = Automatic Calc) | [9 empty] | A or M |  | A
Actuator / VSD Ratio Control Curves
|  | Manual Input | These cells are calculated from the "Application Info" cells above | [6 empty] | Manually Input during Ratio Control Curve Commissioning
CURVE POINTS (Ratio Control) | LMV Curve Point | Gas flow to Burner (Manual Entry / Paste) | Gas flow to Burner (Auto Calc) | LMV Load at Curve Point | Burner Output |  | Burner Head Pressure (Approx) | Boiler Output @ Efficiency | Steam Flow 230o F feed 100 PSIG Steam (Approx) | Air Act Pos | Fuel Act. Pos | VSD Speed | Aux 1 Act Pos | Aux 2 Act Pos | Aux 3 Act Pos | Set Ratio control @ this O2 value (-0, +0.2%)
| # | SCFH | SCFH | % | MM BTU /HR | MW | IN WC | BHP | lb/hr | Deg | Deg | % | Deg | Deg | Deg | % O2 Wet
| 1 | 1166.6667 | 500 | 5 | 0.5 | 0.1464 | 0.025 | 12.696 | 428.9896 | [6 empty] | 0.5
| 2 | 1666.6667 | 1000 | 10 | 1 | 0.2928 | 0.1 | 25.3921 | 857.9792 | [6 empty] | 0.5
| 3 | 3958.3333 | 2125 | 21.25 | 2.125 | 0.6222 | 0.45156 | 53.9582 | 1823.2058 | [6 empty] | 0.5
| 4 | 6250 | 3250 | 32.5 | 3.25 | 0.9516 | 1.0563 | 82.5243 | 2788.4324 | [6 empty] | 0.5
| 5 | 8541.6667 | 4375 | 43.75 | 4.375 | 1.281 | 1.9141 | 111.0904 | 3753.659 | [6 empty] | 0.5
| 6 | 11000 | 5500 | 55 | 5.5 | 1.6104 | 3.025 | 139.6565 | 4718.8856 | [6 empty] | 0.5
| 7 | 13125 | 6625 | 66.25 | 6.625 | 1.9398 | 4.3891 | 168.2226 | 5684.1122 | [6 empty] | 0.5
| 8 | 16000 | 7750 | 77.5 | 7.75 | 2.2692 | 6.0063 | 196.7886 | 6649.3389 | [6 empty] | 0.5
| 9 | 17708.3333 | 8875 | 88.75 | 8.875 | 2.5986 | 7.8766 | 225.3547 | 7614.5655 | [6 empty] | 0.5
| 10 | 20000 | 10000 | 100 | 10 | 2.928 | 10 | 253.9208 | 8579.7921 | [6 empty] | 0.5
%O2 Control - Alarm Curves
From Above |  |  | Based on burner capabilities |  |  | As saved in the LMV52 |  |  |  | Emissions Data from Exhaust Gas Analyzer @ O2 Ratio Control |  |  | Emissions Data from Exhaust Gas Analyzer @ O2 Control
CURVE POINTS (%O2 Control - Alarm) | LMV Curve Point | LMV Load at Curve Point | Target for O2 Control | O2 Alarm (Rich Limit) | O2 MaxValue (Lean Limit) | O2 Ratio Control | O2 Control | Standard Val |  | O2 (Dry) | CO | Nox | O2 (Dry) | CO | Nox
| # | % | % O2 Wet |  |  | % O2 Wet |  | % |  | % | PPM | PPM | % | PPM | PPM
| 1 | 5 | X |  |  | Cannot trim on Point 1 |  |  |  | Cannot trim on Point 1 |  |  | Cannot trim on Point 1
| 2 | 10
| 3 | 21.25
| 4 | 32.5
| 5 | 43.75
| 6 | 55
| 7 | 66.25
| 8 | 77.5
| 9 | 88.75
| 10 | 100
LMV52 Load | Lambda Ratio control Curve | Lambda O2 control curve | Lambda factor | Average Lambdafactor | Standard Dev
| Ratio | Setpoint
10 | 1.0528 | 1.0528 | 0 | 0 | 0
21.25 | 1.0528 | 1.0528 | 0 | 0
32.5 | 1.0528 | 1.0528 | 0 | 0
43.75 | 1.0528 | 1.0528 | 0 | 0
55 | 1.0528 | 1.0528 | 0 | 0
66.25 | 1.0528 | 1.0528 | 0 | 0
77.5 | 1.0528 | 1.0528 | 0 | 0
88.75 | 1.0528 | 1.0528 | 0 | 0
100 | 1.0528 | 1.0528 | 0 | 0

## Manipulated Variable
LMV5 Maximum and Minimim Manipulated Varible
Conditions at Comissioning | Units | Input Data
Ambient Air Temperature at Burner Commissioning | Degrees F | 80
Barometric Pressure at Burner Commissioning | in Hg | 30
Max and Min Temperature
Maximum Expected Ambient Air Temperture | Degrees F | 120
Minimum Expected Ambient Air Temperture | Degrees F | 30
Max and Min Temperature
Maximum Expected Barometric Pressure | in Hg | 31.5
Minimum Expected Barometric Pressure | in Hg | 28
Maximum Manipulated Varible | Unitless | 13.1071
Maximum Manipulated Varible | Unitless | -15.7215
Maximum Manipulated Varible (+5) | Unitless | 18.1071
Maximum Manipulated Varible (-5) | Unitless | -20.7215